## Calculator
Fresh Air Ventilation Calculator
Based on ASHRAE 62.1 2025
Area parameters Input
Area Type |  | Office space
Number of occupants |  | 20
Floor Area (Sq ft ) |  | 3000
OR enter area dimension:
Length (ft)
Width (ft)
Room height (ft) |  | 9
Required Outdoor Air per person (CFM) |  | 5
Required Outdoor Air per square foot (CMF) |  | 0.06
Output
Floor Area (Sq ft ) |  | 3000
Floor Volume (CFM) |  | 27000
Required Fresh Air (Outdoor Air) supply (CFM) |  | 280
Required Total Air supply (Based on 20% Outdoor Air supply) |  | 1400
Air Changes Per Hour (ACH) |  | 3.1111
ACH Outdoor Air |  | 0.62222
Fresh Air Ventilation Calculation for individual areas
Area ID | Area Type | Required OA/person | Required OA/Sq ft | Area (Sq ft) | Occupants | Required CFM | % of total CFM
Room 1 | Office space | 5 | 0.06 | 100 | 2 | 16 | 2.417%
Room 2 | Break rooms | 5 | 0.06 | 50 | 3 | 18 | 2.719%
Room 3 | Classrooms (ages 5 to 8) | 10 | 0.12 | 200 | 10 | 124 | 18.73%
Room 4 | Classrooms (age 9+) | 10 | 0.12 | 200 | 10 | 124 | 18.73%
Room 5 | Conference/meeting | 5 | 0.06 | 200 | 20 | 112 | 16.92%
Room 6 | Lecture hall (fixed seats) | 7.5 | 0.016 | 600 | 30 | 234.6 | 35.43%
Room 7 | Main entry lobbies (office building) | 5 | 0.06 | 100 | 1 | 11 | 1.661%
Room 8 | Occupiable storage rooms for dry materials | 5 | 0.06 | 25 | 1 | 6.5 | 0.9817%
Room 9 | Reception areas | 5 | 0.06 | 100 | 2 | 16 | 2.417%
Room 10 | Office space | 5 | 0.06 |  |  | 0 | 0%
Room 11 | Office space | 5 | 0.06 |  |  | 0 | 0%
Room 12 | Office space | 5 | 0.06 |  |  | 0 | 0%
Room 13 | Office space | 5 | 0.06 |  |  | 0 | 0%
Room 14 | Office space | 5 | 0.06 |  |  | 0 | 0%
Total |  | 82.5 | 0.916 | 1575 | 79 | 662.1 | 100%

## 62.1-2025
Required fresh air for different areas
The amount of fresh air in the breathing zone is calculated by the following formula given in ASHRAE 62.1 2025
Vbz = Rp × Pz + Ra × Az
Where
Rp = flow rate of outdoor air required per person
Pz = zone population, the number of people in the ventilation zone during use
Ra = flow rate of outdoor air required per unit area
Az = zone floor area, the net occupiable floor area of the ventilation zone, ft2
Area | Cfm/person | Cfm/ft2
Classrooms (ages 5 to 8) | 10 | 0.12
Classrooms (age 9+) | 10 | 0.12
Corridors (ages 5+) | 10 | 0.12
Lecture hall (fixed seats) | 7.5 | 0.016
Break rooms | 5 | 0.06
Conference/meeting | 5 | 0.06
Main entry lobbies (office building) | 5 | 0.06
Occupiable storage rooms for dry materials | 5 | 0.06
Office space | 5 | 0.06
Reception areas | 5 | 0.06
Courtrooms | 5 | 0.06
Libraries | 5 | 0.12